## Sheet1
SLNO | ItemCode | ItemName | Brand | Model | UOM | Qty | UnitPriceAED | UnitPrice | Margin | Amount | Unitweight | Optional | COO | DeliveryStatus | CRMProductId | CRMProduct
1 |  | 1E+1D+1J [Pump For Duty Point 1000.00 USGPM @ 140.00 PSI] •Fire Pumps: NAFFCO (UL/FM) Horizontal Split Case •Drivers: ODP Motor and Diesel Engine •Jockey Pump: Vertical Multistage - 50 GPM @ 150.00 PSI •Electric Controller: NAFFCO (UL/FM), Y-Delta Open Type Transition, Enclosure: NEMA 2 •Diesel Controller: NAFFCO (UL/FM), Enclosure: NEMA 2 •Jockey Controller: NAFFCO (UL), Enclosure: NEMA 2 •Accessories: Standard | NAFFCO |  | Set | 1 | 138000 | 45123 | 20 | 45123 | 0 | FALSE |  |  |  | 0
1.1 |  | Suction Side |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
1.1.1 |  | OS&Y Gate Valve 8" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 2 | 1720 | 562 | 20 | 1124 | 0 | FALSE |  |  |  | 0
1.1.2 |  | OS&Y Gate Valve 2" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 1 | 610 | 199 | 20 | 199 | 0 | FALSE |  |  |  | 0
1.1.3 |  | OS&Y Gate Valve 10" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 2 | 2660 | 870 | 20 | 1740 | 0 | FALSE |  |  |  | 0
1.2 |  | Delivery side |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
1.2.1 |  | OS&Y Gate Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 2 | 1170 | 383 | 20 | 766 | 0 | FALSE |  |  |  | 0
1.2.2 |  | OS&Y Gate Valve 2" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 1 | 610 | 199 | 20 | 199 | 0 | FALSE |  |  |  | 0
1.2.3 |  | OS&Y Gate Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved, with supervisory switch | SHIELD | SD-OSY200FF-D | Nos | 4 | 1170 | 383 | 20 | 1532 | 0 | FALSE |  |  |  | 0
1.2.4 |  | Check Valve 2" Class 125 Flanged, 200 PSI working UL/FM Approved | SHIELD | SD-NRV200FF-D | Nos | 1 | 240 | 78 | 20 | 78 | 0 | FALSE |  |  |  | 0
1.2.5 |  | Check Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved | SHIELD | SD-NRV200FF-D | Nos | 2 | 950 | 311 | 20 | 622 | 0 | FALSE |  |  |  | 0
1.2.6 |  | Pressure Gauge 0-250 Psi - 3-1/2" (90MM) UL Listed Shield 1" Ball Valve, BSP Double Female Threaded , Brass Nickel Plated - UL Listed | SHIELD | SD-P SDBLVT95 | Nos | 6 | 65 | 21 | 20 | 126 | 0 | FALSE |  |  |  | 0
2 |  | Sprinkler System |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE | 0 | 0 | 0 | 0
2.1 |  | Sprinkler Head 68 Deg. Pendent, 1/2" NPT, Chrome Finish, Quick Response, UL Listed, Model: SD1030C - Shield (24 Nos Spare) | SHIELD |  | Nos | 2172 | 12 | 4 | 20 | 8688 | 0 | FALSE |  |  |  | 0
2.2 |  | Sprinkler Head 79 Deg. Upright, 1/2" NPT, Chrome Finish, Standard Response, UL Listed, Model: SD1015C, Shield (12 Nos Spare) | SHIELD |  | Nos | 875 | 10 | 3 | 20 | 2625 | 0 | FALSE |  |  |  | 0
2.3 |  | Horizontal Sidewall Sprinkler Head 3/4" 68 Deg, Extended Coverage, QR, UL/ULC Listed - SD8220 (6 Nos Spare) | SHIELD |  | Nos | 41 | 23 | 8 | 20 | 328 | 0 | FALSE |  |  |  | 0
2.4 |  | double escuhteon plate; chrome |  |  | Nos | 35 | 10 | 3 | 20 | 105 | 0 | FALSE |  |  |  | 0
2.5 |  | double escuhteon plate for recessed pendent ; chrome |  |  | Nos | 2148 | 30 | 10 | 20 | 21480 | 0 | FALSE |  |  |  | 0
2.6 |  | Alarm Valve Assembly 8" - Wet Alarm Valve 8" (200NB) Flanged, Vertical Mounting, Painted RED - UL /FM, Model: SDH-AVA - Water Motor Alarm Gong, INT 3/4"BSPT, Epoxty Red Powder Coated, UL Listed, Model: SD-GA - Retard Chamber - RC9 - Pressure Switch, Model: SD-PS | SHIELD |  | Set | 1 | 2480 | 811 | 20 | 811 | 0 | FALSE |  |  |  | 0
2.7 |  | OS&Y Gate Valve 8" Class 125 Flanged, 200 PSI working UL/FM Approved, with Tamper switch | SHIELD | SD-NRV200FF-D | Nos | 2 | 1720 | 562 | 20 | 1124 | 0 | FALSE |  |  |  | 0
2.8 |  | OS&Y Gate Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved, with Tamper switch | SHIELD | SD-NRV200FF-D | Nos | 2 | 1170 | 383 | 20 | 766 | 0 | FALSE |  |  |  | 0
2.9 |  | OS&Y Gate Valve 4" Class 125 Flanged, 200 PSI working UL/FM Approved, with Tamper switch | SHIELD | SD-P SDBLVT95 | Nos | 6 | 860 | 281 | 20 | 1686 | 0 | FALSE |  |  |  | 0
2.10 |  | Zone Control Valve 6" - Butterfly valve, Grooved, 300 Psi, 6", UL/FM - SHIELD, Model:SDBV-G300 - Water Flow Switch 6" UL Listed and FM Approved Model; SD-WFD60 -Test and Drain Valve 1" NPT Threaded UL Listed / FM Approved -SHIELD,Model; SD-TDV50T - Pressure Gauge - SD-P1 - 1" Ball Valve - SDBLVT95 -Check Valve 6"/168MM Grooved , 300 PSI working UL/FM Approved-SHIELD,Model; SD-NRV300GG-D | SHIELD |  | Set | 12 | 1520 | 497 | 20 | 5964 | 0 | FALSE |  |  |  | 0
2.11 |  | Zone Control Valve 4" Butterfly valve, Grooved, 300 Psi, 4", UL/FM - SHIELD, Model:SDBV-G300 - Water Flow Switch 4" UL Listed and FM Approved, Model: SD-WFD40 -Test and Drain Valve 1" NPT Threaded UL Listed / FM Approved -SHIELD,Model; SD-TDV50T - Pressure Gauge - SD-P1 - 1" Ball Valve - SDBLVT95 -Check Valve 4"/114MM Grooved , 300 PSI working UL/FM Approved-SHIELD,Model; SD-NRV300GG-D | SHIELD |  | Set | 7 | 1115 | 365 | 20 | 2555 | 0 | FALSE |  |  |  | 0
2.12 |  | Zone Control Valve 3" - Butterfly valve, Grooved, 300 Psi, 3", UL/FM - SHIELD, Model:SDBV-G300 - Water Flow Switch 3" UL Listed and FM Approved,Model; SD-WFD30 -Test and Drain Valve 1" NPT Threaded UL Listed / FM Approved -SHIELD,Model; SD-TDV50T - Pressure Gauge - SD-P1 - 1" Ball Valve - SDBLVT95 -Check Valve 3"/89MM Grooved , 300 PSI working UL/FM Approved-SHIELD,Model; SD-NRV300GG-D | SHIELD |  | Set | 1 | 1026 | 335 | 20 | 335 | 0 | FALSE |  |  |  | 0
2.13 |  | Sprinkler Cabinet suitable for 6 Sprinkler Heads 1/2" - Painted RED RAL3000 | NAFFCO |  | Nos | 1 | 100 | 33 | 20 | 33 | 0 | FALSE |  |  |  | 0
2.14 |  | Sprinkler Cabinet suitable for 12 Sprinkler Heads 1/2" - Painted RED RAL3000 | NAFFCO |  | Nos | 1 | 140 | 46 | 20 | 46 | 0 | FALSE |  |  |  | 0
2.15 |  | Sprinkler Cabinet suitable for 24 Sprinkler Heads 1/2" - Painted RED RAL3000 | NAFFCO |  | Nos | 1 | 180 | 59 | 20 | 59 | 0 | FALSE |  |  |  | 0
2.16 |  | 6"X4 WAY BREECHING INLET, KITEMARK, RED, NAFFCO | NAFFCO | NWR 115 | Nos | 1 | 831 | 272 | 20 | 272 | 0 | FALSE |  |  |  | 0
2.17 |  | Breaching Inlet Cabinet 4 WAY (As per drawing) | NAFFCO |  | Nos | 1 | 1200 | 392 | 20 | 392 | 0 | FALSE | 0 | 0 | 0 | 0
2.18 |  | Check Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved | SHIELD | SD-NRV200FF-D | Nos | 1 | 950 | 311 | 20 | 311 | 0 | FALSE |  |  |  | 0
2.19 |  | - Pressure Gauge - 1" Ball Valve, BSP Double Female Threaded , Brass Nickel Plated - UL Listed | SHIELD | SD-P SDBLVT95 | Nos | 3 | 65 | 21 | 20 | 63 | 0 | FALSE |  |  |  | 0
2.20 |  | Automatic Air Release Valve, 1" FNPT Inlet x 1/2" FNPT Outlet, 175 Psi Water, UL/FM Approved, Model: NF-25ARV - Naffco -1" Ball Valve, BSP Double Female Threaded , Brass Nickel Plated - UL Listed | NAFFCO | NF-25ARV SDBLVT95 | Nos | 3 | 95 | 31 | 20 | 93 | 0 | FALSE |  |  |  | 0
2.21 |  | Bronze OS & Y Gate Vlave, Threaded, 175 Psi, 1 1/2", UL/FM | SHIELD | SDOSY-T | Nos | 2 | 370 | 121 | 20 | 242 | 0 | FALSE |  |  |  | 0
2.22 |  | Bronze OS & Y Gate Vlave, Threaded, 175 Psi, 1", UL/FM | SHIELD | SDOSY-T | Nos | 31 | 230 | 75 | 20 | 2325 | 0 | FALSE |  |  |  | 0
3 |  | FireFighting System |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
3.1 |  | Fire Hose Cabinet Single Door, Surface Mounted (As per the atatched drawing ) Material Inside The Cabinet : - 1"X30 MTR. HOSE REEL, CABINET MOUNTED, AUTOMATIC - CE, KITEMARK, Model: 25NFH-020A - Lock Shield Valve 1" BSPT 11 Pitch with Key -NAFFCO, Model: NLSV25 - 1" PRV, 25 Bar, BSP Double Female Threaded, Spring Type BSI Kiremarked, Model: SD-91430K - 6 KG DP FIRE EXTINGUSHER - CE,KITEMARK & MED, LPCB - Model: NP6 | NAFFCO |  | Set | 24 | 1100 | 360 | 20 | 8640 | 0 | FALSE |  |  |  | 0
3.2 |  | vertical type fire hose cabinet double door, surface mounted (As per the attached drawing 23-367R ) -1"X30 MTR. HOSE REEL, CABINET MOUNTED, AUTOMATIC - CE, KITEMARK,Model; 25 NFH-020A -Lock Shield Valve 1" BSPT 11 Pitch with Key -NAFFCO, Model; NLSV-25 -1" PRV, 25 Bar, BSP Double Female Threaded, Spring Type BSI Kiremarked, Model; SD-91430K -2-1/2" Pressure Reducing Landing Valve, Flange Inlet Model; NWR-122 -FIRE HOSE, 2.5",RED COLOUR WITH GM COUPLING - KITEMARK, Model; NF-DH2 65R -Branchpipe 2-1/2" with BS Male Inlet - KITEMARK,Model; NF-FB-320 -5 KG CO2 FIRE EXTINGUISHER - CE,KITEMARK & MED, LPCB,Model; NC5 -6 KG DP FIRE EXTINGUSHER - CE,KITEMARK & MED, LPCB - 40% Powder, Model; NP6 | NAFFCO |  | Set | 29 | 2900 | 948 | 20 | 27492 | 0 | FALSE | 0 | 0 | 0 | 0
3.3 |  | 6"X4 WAY BREECHING INLET, KITEMARK, RED, NAFFCO | NAFFCO | NWR 115 | Nos | 1 | 831 | 272 | 20 | 272 | 0 | FALSE |  |  |  | 0
3.4 |  | Breaching Inlet Cabinet Stainless Steel (As per Drawing) | NAFFCO |  | Nos | 1 | 1200 | 392 | 20 | 392 | 0 | FALSE |  |  |  | 0
3.5 |  | Check Valve 6" Class 125 Flanged, 200 PSI working UL/FM Approved | SHIELD | SD-NRV200FF-D | Nos | 1 | 950 | 311 | 20 | 311 | 0 | FALSE |  |  |  | 0
3.6 |  | Pressure Gauge 0-250 Psi - 3-1/2" (90MM) UL Listed Shield 1" Ball Valve, BSP Double Female Threaded , Brass Nickel Plated - UL Listed | SHIELD | SD-P SDBLVT95 | Nos | 3 | 65 | 21 | 20 | 63 | 0 | FALSE |  |  |  | 0
3.7 |  | Automatic Air Release Valve, 1" FNPT Inlet x 1/2" FNPT Outlet, 175 Psi Water, UL/FM Approved, Model: NF-25ARV - Naffco -1" Ball Valve, BSP Double Female Threaded , Brass Nickel Plated - UL Listed | NAFFCO | NF-25ARV SDBLVT95 | Nos | 3 | 95 | 31 | 20 | 93 | 0 | FALSE |  |  |  | 0
4 |  | fire hydrant system |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
4.1 |  | Wet Type Fire Hydrant 4" with 2 x 2.5" BRASS Oblique Landing Valve outlet with cap, chain (As per the attached drawing 23-061TH) | NAFFCO | NHYD 060 | Set | 6 | 1220 | 399 | 20 | 2394 | 0 | FALSE |  |  |  | 0
4.2 |  | Self Standing Fire Hose Cabinet, Complete E.G Sheet - Powder coated (As per the attached drawing 23-370R ) Material inside the cabinet: - 2 Nos x 2.5" x 30mtr fire hose with quick coupling, Model: NF-FH65 - 1 Nos x Branchpipe 2-1/2" Model: NF-FB-320 - Hydrant Wrench - Lug Spanner - 4 Nos x 2.5" Coupling Gasket - Fire Axe | NAFFCO | - | Set | 6 | 2500 | 817 | 20 | 4902 | 0 | FALSE |  |  |  | 0
5 |  | FM200 SYSTEM |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
5..1 |  | Main Electrical room at Groun floor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
5.1.1 |  | SHIELD200 369.0L Cylinder Assembly (184.6kg-442.8kg) Complete with 3" Valve and Pressure Gauge Pressure Switch, Cylinder Label & Bracket without LLI | SHIELD | SD-369HFC-03 | Set | 3 | 12139 | 3969 | 20 | 11907 | 0 | FALSE |  |  |  | 0
5.1.2 |  | Cylinder Bracket 900mm Channel Length Suitable for 369L Cylinder | SHIELD | SD-CBKT-790 | Nos | 3 | 247 | 81 | 20 | 243 | 0 | FALSE |  |  |  | 0
5.1.3 |  | HFC-227EA AGENT | SHIELD |  | KG | 765 | 100 | 33 | 20 | 25245 | 0 | FALSE |  |  |  | 0
5.1.4 |  | 3 Inch (80MM) Outlet Adaptor used to 369L Cylinder Valve Outlet | SHIELD | SD-VOA0080 | Nos | 3 | 175 | 57 | 20 | 171 | 0 | FALSE |  |  |  | 0
5.1.5 |  | Removable Electric Actuator c/w Supervisory Switch, 1 Inch Connection | SHIELD | SD-REA-SS | Nos | 1 | 1507 | 493 | 20 | 493 | 0 | FALSE |  |  |  | 0
5.1.6 |  | Manual Actuator with Push to operate | SHIELD | SD-MA0025 | Nos | 1 | 177 | 58 | 20 | 58 | 0 | FALSE | 0 |  |  | 0
5.1.7 |  | Pneumatic Actuator | SHIELD | SD-PA0025 | Nos | 2 | 157 | 51 | 20 | 102 | 0 | FALSE |  |  |  | 0
5.1.8 |  | Discharge Pressure Switch, Shield - SD-DPS-B6-95-2 | SHIELD | SD-DPS-B6-95-2 | Nos | 2 | 560 | 183 | 20 | 366 | 0 | FALSE |  |  |  | 0
5.1.9 |  | 1/2 NPT Socket |  |  | Nos | 2 | 15 | 5 | 20 | 10 | 0 | FALSE
5.1.10 |  | 1/2 NPT Nipple |  |  | Nos | 2 | 20 | 7 | 20 | 14 | 0 | FALSE
5.1.11 |  | Discharge Hose 3 Inch (80MM) c/w Check Valve with Female Swivel Fittings | SHIELD | SD-DHCV0080 | Nos | 3 | 2352 | 769 | 20 | 2307 | 0 | FALSE |  |  |  | 0
5.1.12 |  | Pneumatique actuation flexible hose | SHIELD | SDFLXHS0015 | Nos | 2 | 35 | 11 | 20 | 22 | 0 | FALSE |  |  |  | 0
5.1.13 |  | 1/4' Pneumatic elbew used at slave cylinder valve | SHIELD | SD-ELWFH-092 | Nos | 1 | 510 | 167 | 20 | 167 | 0 | FALSE |  |  |  | 0
5.1.14 |  | 1/4'nipple used at master cyllinder valve | SHIELD | SD-ELWFH-090 | Nos | 4 | 490 | 160 | 20 | 640 | 0 | FALSE |  |  |  | 0
5.1.15 |  | Pneumatic tee | SHIELD | SD-TFH-091 | Nos | 1 | 500 | 163 | 20 | 163 | 0 | FALSE |  |  |  | 0
5.1.16 |  | manfold for -3- cylinder | SHIELD | SD-MF150-100-3 | Nos | 1 | 490 | 160 | 20 | 160 | 0 | FALSE |  |  |  | 0
5.1.17 |  | Discharge nozzle ;brass | SHIELD |  | Nos | 20 | 291 | 95 | 20 | 1900 | 0 | FALSE |  |  |  | 0
5.1.18 |  | FM 200 Warning Signage | SHIELD | SD-FM-WARN | Set | 1 | 330 | 108 | 20 | 108 | 0 | FALSE |  |  |  | 0
5.1.19 |  | FK-5-1-12 Cylinder Lebel 280x180 - UL/FM Approved | SHIELD | SD-FM-LBL | Nos | 1 | 52 | 17 | 20 | 17 | 0 | FALSE |  |  |  | 0
5.1.20 |  | Extinguisher Control Panel (2) Detection (1) Release Area c/w 24VDC Back-up Battery UL Listed | SHIELD | AX-T | Set | 1 | 2700 | 883 | 20 | 883 | 0 | FALSE |  |  |  | 0
5.1.21 |  | Conventional Photoelectric Smoke Detector, UL Listed, Model: S-C2011 - Shield | FIKE | S-C2011 | Nos | 10 | 60 | 20 | 20 | 200 | 0 | FALSE |  |  |  | 0
5.1.22 |  | Abort Switch w/ Back Box , Shield | SHIELD | S111R-AB | Nos | 1 | 350 | 114 | 20 | 114 | 0 | FALSE |  |  |  | 0
5.1.23 |  | Bell 6" Back Box, Shield | SHIELD | FB-1000C6 | Nos | 1 | 60 | 20 | 20 | 20 | 0 | FALSE |  |  |  | 0
5.1.24 |  | Strobe Horn w/ Back Box, Shield | SHIELD | SH-HSIR | Nos | 1 | 310 | 101 | 20 | 101 | 0 | FALSE |  |  |  | 0
5.1.25 |  | Xenon/strobe Light w/ Back Box, Shield | SHIELD | SH-STIR | Nos | 1 | 240 | 78 | 20 | 78 | 0 | FALSE |  |  |  | 0
5.2 |  | Camera Room at Ground Floor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
5.2.1 |  | SHIELD200 106.0L Cylinder Assembly (53.1kg-127.2kg) Complete with 2" Valve and Pressure Gauge Pressure Switch, Cylinder Label & Bracket without LLI | SHIELD | SD-106HFC-02 | Set | 1 | 5000 | 1635 | 20 | 1635 | 0 | FALSE |  |  |  | 0
5.2.2 |  | Cylinder Bracket 600mm Channel Length Suitable for 52L,106L,147L and 180L Cylinder | SHIELD | SD-CBKT-600 | Nos | 1 | 218 | 71 | 20 | 71 | 0 | FALSE |  |  |  | 0
5.2.3 |  | HFC-227EA AGENT | SHIELD |  | KG | 63 | 100 | 33 | 20 | 2079 | 0 | FALSE |  |  |  | 0
5.2.4 |  | Removable Electric Actuator c/w Supervisory Switch, 1 Inch Connection | SHIELD | SD-REA-SS | Nos | 1 | 1507 | 493 | 20 | 493 | 0 | FALSE |  |  |  | 0
5.2.5 |  | Manual Actuator with Push to operate | SHIELD | SD-MA0025 | Nos | 1 | 177 | 58 | 20 | 58 | 0 | FALSE |  |  |  | 0
5.2.6 |  | Discharge Pressure Switch, Shield | SHIELD | SD-DPS-B6-95-1 | Nos | 1 | 560 | 183 | 20 | 183 | 0 | FALSE |  |  |  | 0
5.2.7 |  | Discharge Hose 2 Inch (50MM) with Female Swivel Fittings | SHIELD | SD-DH0050 | Nos | 1 | 428 | 140 | 20 | 140 | 0 | FALSE |  |  |  | 0
5.2.8 |  | Discharge nozzle ;brass | SHIELD |  | Nos | 2 | 291 | 95 | 20 | 190 | 0 | FALSE |  |  |  | 0
5.2.9 |  | FM 200 Warning Signage | SHIELD | SD-FM-WARN | Set | 1 | 330 | 108 | 20 | 108 | 0 | FALSE |  |  |  | 0
5.2.10 |  | FK-5-1-12 Cylinder Lebel 280x180 - UL/FM Approved | SHIELD | SD-FM-LBL | Nos | 1 | 52 | 17 | 20 | 17 | 0 | FALSE |  |  |  | 0
5.2.11 |  | Extinguisher Control Panel (2) Detection (1) Release Area c/w 24VDC Back-up Battery UL Listed | SHIELD | AX-T | Set | 1 | 2700 | 883 | 20 | 883 | 0 | FALSE |  |  |  | 0
5.2.12 |  | Conventional Photoelectric Smoke Detector, UL Listed, Model: S-C2011 - Shield | FIKE | S-C2011 | Nos | 2 | 60 | 20 | 20 | 40 | 0 | FALSE |  |  |  | 0
5.2.13 |  | Abort Switch w/ Back Box , Shield | SHIELD | S111R-AB | Nos | 1 | 350 | 114 | 20 | 114 | 0 | FALSE |  |  |  | 0
5.2.14 |  | Bell 6" Back Box, Shield | SHIELD | FB-1000C6 | Nos | 1 | 60 | 20 | 20 | 20 | 0 | FALSE |  |  |  | 0
5.2.15 |  | Strobe Horn w/ Back Box, Shield | SHIELD | SH-HSIR | Nos | 1 | 310 | 101 | 20 | 101 | 0 | FALSE |  |  |  | 0
5.2.16 |  | Xenon/strobe Light w/ Back Box, Shield | SHIELD | SH-STIR | Nos | 1 | 240 | 78 | 20 | 78 | 0 | FALSE |  |  |  | 0
5.3 |  | ELECTRIC ROOM 1 AT G FLOOR |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
5.3.1 |  | SHIELD200 106.0L Cylinder Assembly (53.1kg-127.2kg) Complete with 2" Valve and Pressure Gauge Pressure Switch, Cylinder Label & Bracket without LLI -SD-106HFC-02 | SHIELD | SD-106HFC-02 | Nos | 1 | 5000 | 1635 | 20 | 1635 | 0 | FALSE |  |  |  | 0
5.3.2 |  | HFC-227EA AGENT | SHIELD |  | Nos | 85 | 100 | 33 | 20 | 2805 | 0 | FALSE |  |  |  | 0
5.3.3 |  | Removable Electric Actuator c/w Supervisory Switch, 1 Inch Connection - SD-REA-SS | SHIELD | SD-REA-SS | Nos | 1 | 1507 | 493 | 20 | 493 | 0 | FALSE |  |  |  | 0
5.3.4 |  | Manual Actuator with Push to operate - SD-MA0025 | SHIELD | SD-MA0025 | Nos | 1 | 177 | 58 | 20 | 58 | 0 | FALSE |  |  |  | 0
5.3.5 |  | Discharge Pressure Switch, Shield - SD-DPS-B6-95-2 | SHIELD | SD-DPS-B6-95-2 | Nos | 1 | 560 | 183 | 20 | 183 | 0 | FALSE |  |  |  | 0
5.3.6 |  | 1/2 NPT Socket |  |  | Nos | 1 | 15 | 5 | 20 | 5 | 0 | FALSE |  |  |  | 0
5.3.7 |  | 1/2 NPT Nipple |  |  | Nos | 1 | 20 | 7 | 20 | 7 | 0 | FALSE |  |  |  | 0
5.3.8 |  | Discharge Hose 2 Inch (50MM) with Female Swivel Fittings - SD-DH0050 | SHIELD | SD-DH0050 | Nos | 1 | 428 | 140 | 20 | 140 | 0 | FALSE |  |  |  | 0
5.3.9 |  | Discharge nozzle ;brass | SHIELD |  | Nos | 4 | 291 | 95 | 20 | 380 | 0 | FALSE |  |  |  | 0
5.3.10 |  | FM 200 Warning Signage - SD-FM-WARN | SHIELD | SD-FM-WARN | Nos | 1 | 330 | 108 | 20 | 108 | 0 | FALSE |  |  |  | 0
5.3.11 |  | Extinguisher Control Panel (2) Detection (1) Release Area c/w 24VDC Back-up Battery UL Listed - AX-T | SHIELD | AX-T | Nos | 1 | 2700 | 883 | 20 | 883 | 0 | FALSE |  |  |  | 0
5.3.12 |  | Conventional Photoelectric Smoke Detector, UL Listed, Model: S-C2011 - Shield | SHIELD | S-C2011 | Nos | 2 | 60 | 20 | 20 | 40 | 0 | FALSE |  |  |  | 0
5.3.13 |  | Abort Switch w/ Back Box , Shield - S111R-AB | SHIELD | S111R-AB | Nos | 1 | 350 | 114 | 20 | 114 | 0 | FALSE |  |  |  | 0
5.3.14 |  | Bell 6" Back Box, Shield - FB-1000C6 | SHIELD | FB-1000C6 | Nos | 1 | 60 | 20 | 20 | 20 | 0 | FALSE |  |  |  | 0
5.3.15 |  | Strobe Horn w/ Back Box, Shield - SH-HSIR | SHIELD | SH-HSIR | Nos | 1 | 310 | 101 | 20 | 101 | 0 | FALSE |  |  |  | 0
5.3.16 |  | Xenon/strobe Light w/ Back Box, Shield - SH-STIR | SHIELD | SH-STIR | Nos | 1 | 240 | 78 | 20 | 78 | 0 | FALSE |  |  |  | 0
5.4 |  | ELECTRIC ROOM 2 AT G FLOOR |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  |  | 0
5.4.1 |  | SHIELD200 106.0L Cylinder Assembly (53.1kg-127.2kg) Complete with 2" Valve and Pressure Gauge Pressure Switch, Cylinder Label & Bracket without LLI -SD-106HFC-02 | SHIELD | SD-106HFC-02 | Nos | 1 | 5000 | 1635 | 20 | 1635 | 0 | FALSE |  |  |  | 0
5.4.2 |  | HFC-227EA AGENT | SHIELD |  | Nos | 85 | 100 | 33 | 20 | 2805 | 0 | FALSE |  |  |  | 0
5.4.3 |  | Removable Electric Actuator c/w Supervisory Switch, 1 Inch Connection - SD-REA-SS | SHIELD | SD-REA-SS | Nos | 1 | 1507 | 493 | 20 | 493 | 0 | FALSE |  |  |  | 0
5.4.4 |  | Manual Actuator with Push to operate - SD-MA0025 | SHIELD | SD-MA0025 | Nos | 1 | 177 | 58 | 20 | 58 | 0 | FALSE |  |  |  | 0
5.4.5 |  | Discharge Pressure Switch, Shield - SD-DPS-B6-95-2 | SHIELD | SD-DPS-B6-95-2 | Nos | 1 | 560 | 183 | 20 | 183 | 0 | FALSE |  |  |  | 0
5.4.6 |  | 1/2 NPT Socket |  |  | Nos | 1 | 15 | 5 | 20 | 5 | 0 | FALSE |  |  |  | 0
5.4.7 |  | 1/2 NPT Nipple |  |  | Nos | 1 | 20 | 7 | 20 | 7 | 0 | FALSE |  |  |  | 0
5.4.8 |  | Discharge Hose 2 Inch (50MM) with Female Swivel Fittings - SD-DH0050 | SHIELD | SD-DH0050 | Nos | 1 | 428 | 140 | 20 | 140 | 0 | FALSE |  |  |  | 0
5.4.9 |  | Discharge nozzle ;brass | SHIELD |  | Nos | 4 | 291 | 95 | 20 | 380 | 0 | FALSE |  |  |  | 0
5.4.10 |  | FM 200 Warning Signage - SD-FM-WARN | SHIELD | SD-FM-WARN | Nos | 2 | 330 | 108 | 20 | 216 | 0 | FALSE |  |  |  | 0
5.4.11 |  | Extinguisher Control Panel (2) Detection (1) Release Area c/w 24VDC Back-up Battery UL Listed - AX-T | SHIELD | AX-T | Nos | 1 | 2700 | 883 | 20 | 883 | 0 | FALSE |  |  |  | 0
5.4.12 |  | Conventional Heat Detector, 135F, UL listed, Model: S-C2013 - Shield | SHIELD | S-C2013 | Nos | 2 | 60 | 20 | 20 | 40 | 0 | FALSE |  |  |  | 0
5.4.13 |  | Abort Switch w/ Back Box , Shield - S111R-AB | SHIELD | S111R-AB | Nos | 1 | 350 | 114 | 20 | 114 | 0 | FALSE |  |  |  | 0
5.4.14 |  | Bell 6" Back Box, Shield - FB-1000C6 | SHIELD | FB-1000C6 | Nos | 1 | 60 | 20 | 20 | 20 | 0 | FALSE |  |  |  | 0
5.4.15 |  | Strobe Horn w/ Back Box, Shield - SH-HSIR | SHIELD | SH-HSIR | Nos | 1 | 310 | 101 | 20 | 101 | 0 | FALSE |  |  |  | 0
5.4.16 |  | Xenon/strobe Light w/ Back Box, Shield - SH-STIR | SHIELD | SH-STIR | Nos | 1 | 240 | 78 | 20 | 78 | 0 | FALSE |  |  |  | 0
6 |  | DDP Charges to Iraq |  |  | Nos | 1 | 146800 | 48000 | 20 | 48000 | 0 | FALSE |  |  |  | 0

## Sheet2
11907
243
25245
171
493
58
102
366
10
14
2307
22
167
640
163
160
1900
108
17
883
200
114
20
101
78
45489