## Sheet1
SLNO | ItemCode | ItemName | Brand | Model | UOM | Qty | UnitPriceAED | UnitPrice | Margin | Amount | Unitweight | Optional | COO | DeliveryStatus | CRMProductId | CRMProduct
1 |  | Fire Pump Set |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0
1.1 |  | COMBINED PUMP SET DUTY PUMP : 1676GPM @ 11.30 BAR / RATED PUMP DUTY: 1500 GPM @ 11.83 BAR JOCKEY PUMP DUTY: 20 GPM @ 12 BAR 1E + 1D + 1J - NAFFCO UL Listed Horizontal Split Case Pump Coupled With Drivers (TEFC Motor & Diesel Engine) + 1 Vertical Multistage Jockey Pump and NAFFCO UL/FM Approved 1 Electric (Y-Delta Open Type Transition, NEMA 2 Enclosure) + NAFFCO UL/FM Approved 1 Diesel (NEMA 2 Enclosure) + NAFFCO UL Listed 1 Jockey Pump Controller (NEMA 2 Enclosure) Standard Accessories |  |  | Set | 1 | 42362 | 42362 | 0 | 42362 | 0 | FALSE |  |  | 0 | Fire Pump
1.2 |  | Suction Side |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
1.2.1 |  | OS&Y Gate Valve 8" Class 125 Flanged, 250 PSI working, Model: SD-OSY250FF-D - UL/ULC/FM Approved - SHIELD |  |  | Nos | 4 | 460.5 | 460.5 | 0 | 1842 | 0 | FALSE |  |  | 0 | Fire Fighting
1.2.2 |  | Supervisory / Tamper Switch |  |  | Nos | 2 | 46 | 46 | 0 | 92 | 0 | FALSE |  |  | 0 | Fire Fighting
1.2.3 |  | OS&Y Gate Valve 2" Class 125 Flanged, 250 PSI working, Model: SD-OSY250FF-D - UL/ULC/FM Approved - SHIELD |  |  | Nos | 1 | 125.35 | 125.35 | 0 | 125.35 | 0 | FALSE |  |  | 0 | Fire Fighting
1.2.4 |  | Supervisory / Tamper Switch |  |  | Nos | 1 | 46 | 46 | 0 | 46 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3 |  | Delivery Side |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0
1.3.1 |  | OS&Y Gate Valve 8" Class 125 Flanged, 250 PSI working, Model: SD-OSY250FF-D - UL/ULC/FM Approved - SHIELD |  |  | Nos | 2 | 460.5 | 460.5 | 0 | 921 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.2 |  | Supervisory / Tamper Switch |  |  | Nos | 2 | 46 | 46 | 0 | 92 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.3 |  | OS&Y Gate Valve 2" Class 125 Flanged, 250 PSI working, Model: SD-OSY250FF-D - UL/ULC/FM Approved - SHIELD |  |  | Nos | 1 | 125.35 | 125.35 | 0 | 125.35 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.4 |  | Supervisory / Tamper Switch |  |  | Nos | 1 | 46 | 46 | 0 | 46 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.5 |  | Check Valve 2" Class 125 Flanged, 300 PSI working, Model: SD-NRV300FF-D - UL/FM Approved - SHIELD |  |  | Nos | 1 | 65.5 | 65.5 | 0 | 65.5 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.6 |  | Check Valve 8" Class 125 Flanged, 300 PSI working, Model: SD-NRV300FF-D - UL/FM Approved - SHIELD |  |  | Nos | 2 | 524 | 524 | 0 | 1048 | 0 | FALSE |  |  | 0 | Fire Fighting
1.3.7 |  | Pressure Gauge + Isolation Valve |  |  | Nos | 6 | 41 | 41 | 0 | 246 | 0 | FALSE |  |  | 0 | Fire Fighting
2 |  | FIRE FIGHTING SYSTEM |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
2.1 |  | DOUBLE VERTICAL FIRE HOSE REEL CABINET, RECESSED TYPE, 1.5MM STAINLESS STEEL FACIA, BACK BOX MILD STEEL, SOLID DOOR WITH PAINO HINGES |  |  | Nos | 6 | 322.6349 | 322.6349 | 0 | 1935.8095 | 0 | FALSE |  |  | 0 | Fire Fighting
2.2 |  | Right Compartment: Fire Hose Reel 1" x 30 Mtr. Cabinet Mounted, Automatic with Plastic Nozzle, Kitemark /LPCB Approved, Model: 25 NFH-020A - Naffco, UAE |  |  | Nos | 6 | 117.224 | 117.224 | 0 | 703.3441 | 0 | FALSE |  |  | 0 | Fire Fighting
2.3 |  | Globe Valve, Threaded, 175 Psi, 1", UL, Model: SD-GV, Shield |  |  |  | 6 | 19.3581 | 19.3581 | 0 | 116.1486 | 0 | FALSE |  |  | 0 | Fire Fighting
2.4 |  | 1" PRV, 25 Bar, BSP Double Female Threaded, Spring Type, Model: SD-91430K - BSI Kiremarked - Shield |  |  | Nos | 6 | 24.6681 | 24.6681 | 0 | 148.0088 | 0 | FALSE |  |  | 0 | Fire Fighting
2.5 |  | Lower Compartment: Dry Powder Extinguisher Portable Pressure Type, Capacity 9 Kg, Red Color, CE/KITEMARK/MED/LPCB Approved, Model: NP9 - Naffco, UAE |  |  | Nos | 6 | 30.3815 | 30.3815 | 0 | 182.2887 | 0 | FALSE |  |  | 0 | Fire Fighting
2.6 |  | CO2 Extinguisher Portable Type, Capacity: 5 Kg, Red Color, CE/KITEMARK/MED/LPCB Approved, Model: NC 5 - Naffco, UAE |  |  | Nos | 6 | 42.7449 | 42.7449 | 0 | 256.4696 | 0 | FALSE |  |  | 0 | Fire Fighting
2.7 |  | Pressure Gauge + Isolation Valve |  |  | Nos | 6 | 40.4557 | 40.4557 | 0 | 242.7344 | 0 | FALSE |  |  | 0 | Fire Fighting
2.8 |  | DOUBLE VERTICAL FIRE HOSE REEL CABINET, SURFACE MOUNTED, 1.5MM COMPLETE MILD STEEL, SOLID DOOR. With Bush Hinges |  |  | Nos | 7 | 174.7606 | 174.7606 | 0 | 1223.3241 | 0 | FALSE |  |  | 0 | Fire Fighting
2.9 |  | Right Compartment: Fire Hose Reel 1" x 30 Mtr. Cabinet Mounted, Automatic with Plastic Nozzle, Kitemark /LPCB Approved, Model: 25 NFH-020A - Naffco, UAE |  |  | Nos | 7 | 117.224 | 117.224 | 0 | 820.5682 | 0 | FALSE |  |  | 0 | Fire Fighting
2.10 |  | Globe Valve, Threaded, 175 Psi, 1", UL, Model: SD-GV, Shield |  |  | Nos | 7 | 19.3581 | 19.3581 | 0 | 135.5067 | 0 | FALSE |  |  | 0 | Fire Fighting
2.11 |  | 1" PRV, 25 Bar, BSP Double Female Threaded, Spring Type, Model: SD-91430K - BSI Kiremarked - Shield |  |  | Nos | 7 | 24.6681 | 24.6681 | 0 | 172.6769 | 0 | FALSE |  |  | 0 | Fire Fighting
2.12 |  | Lower Compartment: Dry Powder Extinguisher Portable Pressure Type, Capacity 9 Kg, Red Color, CE/KITEMARK/MED/LPCB Approved, Model: NP9 - Naffco, UAE |  |  | Nos | 7 | 30.3815 | 30.3815 | 0 | 212.6702 | 0 | FALSE |  |  | 0 | Fire Fighting
2.13 |  | CO2 Extinguisher Portable Type, Capacity: 5 Kg, Red Color, CE/KITEMARK/MED/LPCB Approved, Model: NC 5 - Naffco, UAE |  |  | Nos | 7 | 42.7449 | 42.7449 | 0 | 299.2145 | 0 | FALSE |  |  | 0 | Fire Fighting
2.14 |  | Pressure Gauge + Isolation Valve |  |  | Nos | 7 | 40.4557 | 40.4557 | 0 | 283.1901 | 0 | FALSE |  |  | 0 | Fire Fighting
2.15 |  | Upright Sprinkler Head, 1/2" Quick Response, Brass Finish, UL/ULC Listed, Model: SD1032 QR - Shield Temperature Rating: 68⁰C |  |  | Nos | 356 | 2.9575 | 2.9575 | 0 | 1052.8653 | 0 | FALSE |  |  | 0 | Fire Fighting
2.16 |  | Concealed Pendent Sprinkler Head, 1/2" Quick Response, Painted Finish, UL/ULC Listed, Model: SD1055 QR - Shield with Concealed Cover plate 57°C - Painted Finish Temperature Rating: 68⁰C |  |  | Nos | 248 | 10.4319 | 10.4319 | 0 | 2587.1019 | 0 | FALSE |  |  | 0 | Fire Fighting
2.17 |  | Wet Alarm Valve Assembly 4", Basic Trim: Vertical, Retard Chamber & Motor Alarm Gong, Pressure Switch & Pressure Gauge, Model: SDH-AVA - Shield |  |  | Nos | 1 | 747.6607 | 747.6607 | 0 | 747.6607 | 0 | FALSE |  |  | 0 | Fire Fighting
2.18 |  | Zone Control Valve 3": OS&Y Valve W/ Supervisory Switch, Flow Switch, Test & Drain Valve, Pressure Gauge, UL/FM Approved - Shield |  |  | Nos | 6 | 309.1918 | 309.1918 | 0 | 1855.1508 | 0 | FALSE |  |  | 0 | Fire Fighting
2.19 |  | Zone Control Valve 6": OS&Y Valve W/ Supervisory Switch, Flow Switch, Test & Drain Valve, Pressure Gauge, UL/FM Approved - Shield |  |  | Nos | 3 | 343.3804 | 343.3804 | 0 | 1030.1411 | 0 | FALSE |  |  | 0 | Fire Fighting
2.20 |  | Breeching Inlet 6", Flanged Inlet, 4-Way 2-1/2", C.I / Ductile Iron Red Painted, BS 5041, Kitemark, Model: NWR-115 - Naffco, UAE |  |  | No | 1 | 191.4247 | 191.4247 | 0 | 191.4247 | 0 | FALSE |  |  | 0 | Fire Fighting
2.21 |  | Breaching Inlet Cabinet Stainless Steel Facia w/ Glass door, 600 x 600 x 300 |  |  | No | 1 | 185.5151 | 185.5151 | 0 | 185.5151 | 0 | FALSE |  |  | 0 | Fire Fighting
3 |  | Wet Chemical Fire Suppression System |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
3.1 |  | Kitchen System Charged Cylinder (10 Flow Point) w/Valve, Model: NF-KS10 - NAFFCO |  |  | No | 1 | 313.8965 | 313.8965 | 0 | 313.8965 | 0 | FALSE |  |  | 0 | Fire Fighting
3.2 |  | BFR-CAP - Valve Cap Assembly, Model: NFR-CAP - NAFFCO |  |  | No | 1 | 29.9728 | 29.9728 | 0 | 29.9728 | 0 | FALSE |  |  | 0 | Fire Fighting
3.3 |  | Mounting Bracket Model: MB-2 |  |  | No | 1 | 49.0463 | 49.0463 | 0 | 49.0463 | 0 | FALSE |  |  | 0 | Fire Fighting
3.4 |  | System Releasing Module w/ Single Fusible Link Line for Kitchen System Model: NFKS-SRM |  |  | No | 1 | 211.1717 | 211.1717 | 0 | 211.1717 | 0 | FALSE |  |  | 0 | Fire Fighting
3.5 |  | Remote Mechanical Pull Station for Kitchen System, Model: NFKS-RPSM |  |  | Nos | 1 | 55.8583 | 55.8583 | 0 | 55.8583 | 0 | FALSE |  |  | 0 | Fire Fighting
3.6 |  | Fusible Link - 360 Deg.F, Model: FL-360 |  |  | Nos | 4 | 4.3597 | 4.3597 | 0 | 17.4387 | 0 | FALSE |  |  | 0 | Fire Fighting
3.7 |  | Fusible Link Holder, Model: FLH |  |  | Nos | 4 | 4.0872 | 4.0872 | 0 | 16.3488 | 0 | FALSE |  |  | 0 | Fire Fighting
3.8 |  | Fusible Link Bracket Kit, Model: FLB |  |  | Nos | 4 | 9.5368 | 9.5368 | 0 | 38.1471 | 0 | FALSE |  |  | 0 | Fire Fighting
3.9 |  | Low Proximity Nozzle (1 Flow Point), Model: N-1LP |  |  | Nos | 4 | 27.248 | 27.248 | 0 | 108.9918 | 0 | FALSE |  |  | 0 | Fire Fighting
3.10 |  | High Proximity Nozzle (1 Flow Point), Model: N-1HP |  |  | No | 1 | 27.248 | 27.248 | 0 | 27.248 | 0 | FALSE |  |  | 0 | Fire Fighting
3.11 |  | High Proximity Nozzle (2 Flow Point), Model: N-2HP |  |  | No | 1 | 27.248 | 27.248 | 0 | 27.248 | 0 | FALSE |  |  | 0 | Fire Fighting
3.12 |  | Wide Angle Nozzle (2 Flow Point), Model: N-2W |  |  | No | 1 | 28.6104 | 28.6104 | 0 | 28.6104 | 0 | FALSE |  |  | 0 | Fire Fighting
3.13 |  | Hood Quickseal, Compression Type for 3/8" (17.1mm OD) PIPE - CQS-38P |  |  | No | 1 | 24.5232 | 24.5232 | 0 | 24.5232 | 0 | FALSE |  |  | 0 | Fire Fighting
3.14 |  | Hood Quickseal, Compression Type for 1/2" (1.3cm) EMT - CQS-50C |  |  | No | 1 | 23.1608 | 23.1608 | 0 | 23.1608 | 0 | FALSE |  |  | 0 | Fire Fighting
3.15 |  | Comp Corner Pulley, CPCT-1 |  |  | Nos | 12 | 6.812 | 6.812 | 0 | 81.7439 | 0 | FALSE |  |  | 0 | Fire Fighting
3.16 |  | Hood QS - Corner Pulley Adaptor - QS-CPA |  |  | Nos | 12 | 13.8965 | 13.8965 | 0 | 166.7575 | 0 | FALSE |  |  | 0 | Fire Fighting
3.17 |  | Cable, 1/16" (0.16Cm), S/Steel with Flexible Conduit for Kitchen System, 100' Roll, Model: NFR-SC-100 |  |  | No | 1 | 4.0872 | 4.0872 | 0 | 4.0872 | 0 | FALSE |  |  | 0 | Fire Fighting
3.18 |  | Swivel Nozzle Adaptor, Model: N-SA |  |  | Nos | 5 | 47.6839 | 47.6839 | 0 | 238.4196 | 0 | FALSE |  |  | 0 | Fire Fighting
3.19 |  | Shielded S/Steel Cable Interface |  |  | Nos | 6 | 6.812 | 6.812 | 0 | 40.8719 | 0 | FALSE |  |  | 0 | Fire Fighting
3.20 |  | 3/8" Stainless Steel Pipe - SS 316 |  |  | Nos | 2 | 149.8638 | 149.8638 | 0 | 299.7275 | 0 | FALSE |  |  | 0 | Fire Fighting
3.21 |  | 1/4" Copper Tube |  |  | Mtr | 1 | 47.6839 | 47.6839 | 0 | 47.6839 | 0 | FALSE |  |  | 0 | Fire Fighting
3.22 |  | 3/8" Elbow |  |  | Nos | 12 | 4.6322 | 4.6322 | 0 | 55.5858 | 0 | FALSE |  |  | 0 | Fire Fighting
3.23 |  | 3/8" Tee |  |  | Nos | 7 | 4.0872 | 4.0872 | 0 | 28.6104 | 0 | FALSE |  |  | 0 | Fire Fighting
3.24 |  | ½" EMT Conduit |  |  | Mtr | 12 | 6.5395 | 6.5395 | 0 | 78.4741 | 0 | FALSE |  |  | 0 | Fire Fighting
3.25 |  | Warning Sign |  |  | Nos | 6 | 27 | 27 | 0 | 162 | 0 | FALSE |  |  | 0 | Fire Fighting
4 |  | HFC227ea - Modular System(Elec. room) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1 |  | Mechanical Component |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1.1 |  | 150 LBS. HFC227EA AGENT CYLINDER - C/W: IMPULSE DISCHARGE VALVE, NIPPLE, VICTAULIC COUPLING, MOUNTING STRAP, PRESSURE GAUGE, UL/FM APPROVED, NAFFCO - UAE |  |  | Set | 1 | 1600 | 1600 | 0 | 1600 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1.2 |  | HFC227EA GAS / LBS |  |  | Lbs | 150.5 | 10 | 10 | 0 | 1505 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1.3 |  | IMPULSE VALVE OPERATOR W/MANUAL STRIKE BUTTON KIT C/W: IMPULSE VALVE OPERATOR, MODEL: NF-02-12728, RESET TOOL, MODEL: 70-286, WIRE LEAD W/CONNECTOR, MODEL: 02-12755, IMPULSE RELEASE MODULE, MODEL: NF-10-2748 |  |  | Set | 1 | 350 | 350 | 0 | 350 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1.4 |  | PRESSURE SWITCH (LOW), MODEL: 02-12533 |  |  | Nos | 1 | 115 | 115 | 0 | 115 | 0 | FALSE |  |  | 0 | Fire Fighting
4.1.5 |  | DISCHARGE NOZZLE |  |  | Nos | 1 | 55 | 55 | 0 | 55 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2 |  | Electrical Component |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.1 |  | EXTINGUISING CONTROL PANEL (2) DETECTION ZONE AND RELEASING AREA (1) C/W 24VDC BACK-UP BATTERY, MODEL: EX-T- SHIELD |  |  | Set | 1 | 500 | 500 | 0 | 500 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.2 |  | SMOKE DETECTORW/ BACK BOX, MODEL: S-C2011 |  |  | Nos | 2 | 13.3515 | 13.3515 | 0 | 26.703 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.3 |  | ABORT SWITCH W/ BACK BOX, MODEL: S111R-AB |  |  | No | 1 | 80 | 80 | 0 | 80 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.4 |  | FIRE ALARM BELL 6", MODEL: FB1000C6 |  |  | No | 1 | 15 | 15 | 0 | 15 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.5 |  | STROBE HORN W/BACK BOX, |  |  | No | 1 | 61 | 61 | 0 | 61 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.6 |  | STROBE LIGHT W/ BACK BOX, |  |  | No | 1 | 49 | 49 | 0 | 49 | 0 | FALSE |  |  | 0 | Fire Fighting
4.2.7 |  | WARNING SIGN |  |  | Nos | 3 | 27 | 27 | 0 | 81 | 0 | FALSE |  |  | 0 | Fire Fighting
5 |  | HFC227ea - Modular System(Server room) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1 |  | Mechanical Component |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1.1 |  | 60 LBS. HFC227EA AGENT CYLINDER - C/W: IMPULSE DISCHARGE VALVE, NIPPLE, VICTAULIC COUPLING, MOUNTING STRAP, PRESSURE GAUGE, UL/FM APPROVED, NAFFCO - UAE |  |  | Set | 1 | 1200 | 1200 | 0 | 1200 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1.2 |  | HFC227EA GAS / LBS |  |  | Lbs | 55 | 10 | 10 | 0 | 550 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1.3 |  | IMPULSE VALVE OPERATOR W/MANUAL STRIKE BUTTON KIT C/W: IMPULSE VALVE OPERATOR, MODEL: NF-02-12728, RESET TOOL, MODEL: 70-286, WIRE LEAD W/CONNECTOR, MODEL: 02-12755, IMPULSE RELEASE MODULE, MODEL: NF-10-2748 |  |  | Set | 1 | 350 | 350 | 0 | 350 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1.4 |  | PRESSURE SWITCH (LOW), MODEL: 02-12533 |  |  | Nos | 1 | 115 | 115 | 0 | 115 | 0 | FALSE |  |  | 0 | Fire Fighting
5.1.5 |  | DISCHARGE NOZZLE |  |  | Nos | 2 | 55 | 55 | 0 | 110 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2 |  | Electrical Component |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.1 |  | EXTINGUISING CONTROL PANEL (2) DETECTION ZONE AND RELEASING AREA (1) C/W 24VDC BACK-UP BATTERY, MODEL: EX-T- SHIELD |  |  | Nos | 1 | 500 | 500 | 0 | 500 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.2 |  | SMOKE DETECTORW/ BACK BOX, MODEL: S-C2011 |  |  | Nos | 4 | 13.3515 | 13.3515 | 0 | 53.406 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.3 |  | ABORT SWITCH W/ BACK BOX, MODEL: S111R-AB |  |  | Nos | 1 | 80 | 80 | 0 | 80 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.4 |  | FIRE ALARM BELL 6", MODEL: FB1000C6 |  |  | Nos | 1 | 15 | 15 | 0 | 15 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.5 |  | STROBE HORN W/BACK BOX, |  |  | Nos | 1 | 61 | 61 | 0 | 61 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.6 |  | STROBE LIGHT W/ BACK BOX, |  |  | Nos | 1 | 49 | 49 | 0 | 49 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.7 |  | REMOTE INDICATOR, MODEL: RA 100Z |  |  | Nos | 2 | 16.3488 | 16.3488 | 0 | 32.6975 | 0 | FALSE |  |  | 0 | Fire Fighting
5.2.8 |  | WARNING SIGN |  |  | Nos | 3 | 27 | 27 | 0 | 81 | 0 | FALSE |  |  | 0 | Fire Fighting