## IG 541
SLNO | ItemCode | ItemName | Brand | Model | UOM | Qty | UnitPriceAED | UnitPrice | Margin | Amount | Unitweight | Optional | COO | DeliveryStatus | CRMProductId | CRMProduct
1 |  | INERT GAS SUPPRESSION SYSTEM - IG-100, 300 BAR SYSTEM - CENTRAL BANKING @ GIS SUBSTATION |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
1.1 |  | MECHANICAL COMPONENTS (MAIN) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
1.1.1 |  | 140 LITER, 300 BAR INERT GAS CYLINDER - MODEL: NF IG541-300-140 - NAFFCO COMPLETE WITH: - 140 LITER 356 MM DIA. CYLINDER FILLED WITH FILLED WITH IG-100 AGENT - 300 BAR DISCHARGE HEAD VALVE WITH PRESSURE GAUGE/PRESSURE SWITCH FOR 300 BAR; SAFETY PROTECTION CAP - CYLINDER ID LABEL FOR 300 BAR, IG 100 GAS, 140 LITER CONSTANTS PRESSURE REGULATOR FOR 200/300 BAR WITH GASKET | NAFFCO | NF IG100-300-140 | SETS | 31 | 4770 | 1365 | 0 | 42315 | 0 | FALSE |  |  | 0 | NULL
1.1.2 | 10341512133 | ELECTRO MAGNETIC DEVICE WITH DIODE, INLET THREADED TO M42 X 1.5, 24V DC, 0.5 A, IP 65 RATED, P/N.# B04425146 FOR UL LISTED FIRE SUPPRESSION SYSTEM (REFER ITEM.# 10341512136) | NAFFCO | B04425148 | NOS | 4 | 790 | 227 | 0 | 908 | 0 | FALSE |  |  | 0 | NULL
1.1.3 | 10349012810 | RESET TOOL FOR ELECTRO MAGNETIC DEVICE FOR INERT GAS SYSTEM, P/N.# 029210064 (OLD P/N.# 023000064) - NAFFCO | NAFFCO | 029210064 (023000064) | NOS | 4 | 110 | 32 | 0 | 128 | 0 | FALSE |  |  | 0 | NULL
1.1.4 | 10341512520 | MONITORING SWITCH FOR ELECTROMAGNETIC DEVICE FOR UL LISTED NAFFCOINERT SYSTEM, PART NO: 029905200-NF - NAFFCO | NAFFCO | 029905200-NF | NOS | 4 | 350 | 101 | 0 | 404 | 0 | FALSE |  |  | 0 | NULL
1.1.5 | 10341512120 | MANUAL / PNEUMATIC RELEASE DEVICE, WP 300 BAR, INLET THREADED TO M42 X 1.5, PNEUMATIC LINE CONNECTION G 1/8", P/N.# B04420065-NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B04420065 | NOS | 4 | 120 | 35 | 0 | 140 | 0 | FALSE |  |  | 0 | NULL
1.1.6 | 10341512122 | PNEUMATIC RELEASE DEVICE, WP 300 BAR, INLET THREADED TO M42 X 1.5, PNEUMATIC LINE CONNECTION G 1/8", P/N.# B04420066NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B04420066 | NOS | 27 | 80 | 23 | 0 | 621 | 0 | FALSE |  |  | 0 | NULL
1.1.7 | 10343512025 | DISCHARGE HOSE, DN16, WP 350 BAR, B/P 1400 BAR, 400MM LENGTH, INLET FEMALE THREAD TO W 21.8 X 1/14" TO DIN 477 & OUTLET FEMALE THREAD TO G 3/4", P/N.# B06920225-NF FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM | NAFFCO | B06920225-NF | NOS | 31 | 180 | 52 | 0 | 1612 | 0 | FALSE |  |  | 0 | NULL
1.1.8 | 10343012208 | MANIFOLD CHECK VALVE, BRASS, MAX W/P 100 BAR, TP 150 BAR, HOSE CONNECTION THREAD G3/4", MANIFOLD CONNECTION THREAD R1" DN12, P/N.# B04600008-NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B04600008 | NOS | 31 | 130 | 38 | 0 | 1178 | 0 | FALSE |  |  | 0 | NULL
1.1.9 | 10343512032 | PILOT HOSE, SYNTHETIC RUBBER OIL RESISTANT W/STRAIGHT FITTINGS M12 X 1.5 FEMALE THREAD IN BOTH ENDS, 700MM LONG, W/P 400 BAR, B/P 1600 BAR, TEMP RANGE: -40 C. TO 100 C, P/N.# B06920212 FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B06920212-NF | NOS | 12 | 70 | 21 | 0 | 252 | 0 | FALSE |  |  | 0 | NULL
1.1.10 | 10343512033 | PILOT HOSE, SYNTHETIC RUBBER OIL RESISTANT W/STRAIGHT FITTINGS M12 X 1.5 FEMALE THREAD IN BOTH ENDS, 500MM LONG, W/P 400 BAR, B/P 1600 BAR, TEMP RANGE: -40 C. TO 100 C, P/N.# B06920213 FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B06920213-NF | NOS | 18 | 70 | 21 | 0 | 378 | 0 | FALSE |  |  | 0 | NULL
1.1.11 | 10349012606 | CONNECTING ADAPTOR, M12 X 1.5 MALE THREADED & G 1/8" MALE THREADED, P/N.# 029510006 FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | 029510006 | NOS | 30 | 20 | 6 | 0 | 180 | 0 | FALSE |  |  | 0 | NULL
1.1.12 | 10346012640 | BLEED VALVE, P/N.# 029730040-NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | 029730040 | NOS | 4 | 170 | 49 | 0 | 196 | 0 | FALSE |  |  | 0 | NULL
1.1.13 |  | MANIFOLD FOR 3 CYLINDER NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM, 360 DIA CYLINDER, P/N.# NFIG-360-SRM3 - NAFFCO | NAFFCO | NFIG-360-SRM3 | NOS | 2 | 880 | 252 | 0 | 504 | 0 | FALSE |  |  | 0 | NULL
1.1.14 | 10344012325 | MANIFOLD FOR 5 CYLINDER NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM, 360 DIA CYLINDER, P/N.# NFIG-360-SRM5 - NAFFCO | NAFFCO | NFIG-360-SRM5 | NOS | 5 | 1060 | 304 | 0 | 1520 | 0 | FALSE |  |  | 0 | NULL
1.1.15 | 10342513010 | SELECTOR VALVE 1" (25MM), MODEL: B05511050-NF - NAFFCO | NAFFCO | B05511050-NF | NOS | 2 | 3540.2175 | 1013 | 0 | 2026 | 0 | FALSE |  |  | 0 | NULL
1.1.16 | 10342513020 | SELECTOR VALVE 2" (50MM), MODEL: B05511250-NF - NAFFCO | NAFFCO | B05511250-NF | NOS | 1 | 4796.9375 | 1373 | 0 | 1373 | 0 | FALSE |  |  | 0 | NULL
1.1.17 | 10342513030 | SELECTOR VALVE 3" (80MM), MODEL: B05511450-NF - NAFFCO | NAFFCO | B055115450-NF | NOS | 1 | 12455.9375 | 3564 | 0 | 3564 | 0 | FALSE |  |  | 0 | NULL
1.1.18 |  | PILOT CYLINDER ASSEMBLY (FOR MIULTI-ZONE) MAIN+STANDBY COMPLETE WITH ALL ACCESSORIES REQUIRED FOR THIS ASSEMBLY: - HIGH PRESSURE PRMIARY REGULATOR (SET PRESSURE - 6 TO 10 BAR) UL LISTED - 1/4" HIGH PRESSURE PILOT HOSE - CONSTANT FLOW PRESSURE DISHARGE REGULATOR - B8400003-NF - DISCHARGE VALVE, PART NUMBER: B04801218-NF - ELECTROMAGNETIC RELEASE DEVICE, PART NUMBER: B044425146-NF - MANUAL/PNEUMATIC RELEASE DEVICE, PART NUMBER: B04420065-NF - PRESSURE GAUGE, PART NUMBER: 029720221-NF - PILOT CYLINDER, W28.8x14TPI THREADS TO 25E EN ISO 113631-1 - POP OFF VALVE, SET PRESSURE 175 PSI 1/2" CARBON STEEL 300 BAR RATED CHECK VALVE HIGH PRESSURE FITTINGS, HOSE & OTHER ACCESSORIES TO COMPLETE THE ASSEMBLY | NAFFCO |  | NOS | 8 | 6935.9419 | 1985 | 0 | 15880 | 0 | FALSE |  |  | 0 | NULL
1.1.19 | 10344212380 | RACK ASSEMBLY FOR 10 CYLINDERS, DOUBLE ROW, FLOOR MOUNTING TYPE, CYLINDER DIA: 360MM, CAPACITY: 67L, 80L & 140L, PRESSURE RATING: 200 / 300BAR, MODEL: NFIG-RA02-050F FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM - NAFFCO | NAFFCO | NFIG-RA02-050F | NOS | 2 | 680 | 195 | 0 | 390 | 0 | FALSE |  |  | 0 | NULL
1.1.20 |  | RACK ASSEMBLY FOR 3 CYLINDERS, SINGLE ROW, FLOOR MOUNTING TYPE, CYLINDER DIA: 267MM, CAPACITY: 67L, 80L & 140L, PRESSURE RATING: 200 / 300BAR, MODEL: NFIG-RA01-003F FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM - NAFFCO | NAFFCO | NFIG-RA01-003F | NOS | 2 | 460 | 132 | 0 | 264 | 0 | FALSE |  |  | 0 | NULL
1.1.21 |  | RACK ASSEMBLY FOR 5 CYLINDERS, SINGLE ROW, FLOOR MOUNTING TYPE, CYLINDER DIA: 267MM, CAPACITY: 67L, 80L & 140L, PRESSURE RATING: 200 / 300BAR, MODEL: NFIG-RA01-005F FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM - NAFFCO | NAFFCO | NFIG-RA01-005F | NOS | 1 | 500 | 144 | 0 | 144 | 0 | FALSE |  |  | 0 | NULL
1.1.22 |  | DISCHARGE NOZZLE | NAFFCO | NAFFCO | NOS | 40 | 180 | 52 | 0 | 2080 | 0 | FALSE |  |  | 0 | NULL
1.1.23 | 10341512137 | PRESSURE RELIEF DEVICE FOR MANIFOLD, P/N.# 029730037 FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM | NAFFCO | P/N #29730037 | NOS | 1 | 1900 | 544 | 0 | 544 | 0 | FALSE |  |  | 0 | NULL
1.1.24 | 10341512022 | PRESSURE & FLOW DETECTOR SWITCH, P/N.# 028250050 FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM | NAFFCO | P/N # 28250050 | NOS | 4 | 690 | 198 | 0 | 792 | 0 | FALSE |  |  | 0 | NULL
1.1.25 |  | CHECK VALVE IN CYLINDER MANIFOLD/MAIN RESERVE HEADER PIPE - 2" | NAFFCO | 504.110008BI | NOS | 1 | 727.3048 | 209 | 0 | 209 | 0 | FALSE |  |  | 0 | NULL
1.1.26 |  | STOP MAINTENANCE VALVE, SIZE: DN25, THREAD SIZE: G 1" WITH CARBON STEEL HOUSING AND SS BALL C/W SUPERVISORY SWITCH, 24V DC/240V AC, PW 315BAR, P/N# B05512300-NF - NAFFCO | NAFFCO | B05512300-NF | NOS | 1 | 5000 | 1431 | 0 | 1431 | 0 | FALSE |  |  | 0 | NULL
1.2 |  | ELECTRICAL COMPONENTS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
1.2.1.2 |  | 2 LOOP ADDRESSABLE FIRE EXTINGUISHING PANEL, COMPLETE WITH: 24V DC BACK UP BATTERY WITH 75 AH BATTERY ENCLOSURE 2 NOS. CRM4 RELAY MODULE | Cheetah Xi - FIKE | 10-068-R-2-L | SETS | 1 | 8500 | 2432 | 0 | 2432 | 0 | FALSE |  |  | 0 | NULL
1.2.1.3 |  | PHOTOELECTRIC SMOKE DETECTOR w/base | FIKE | 63-1058 & 63-1061 | NOS | 36 | 450 | 129 | 0 | 4644 | 0 | FALSE |  |  | 0 | NULL
1.2.1.4 |  | PROBE TYPE HEAT DETECTOR WITH BASE | FIKE | 60-008 | NOS | 8 | 450 | 129 | 0 | 1032 | 0 | FALSE |  |  | 0 | NULL
1.2.1.5 |  | MANUAL RELEASE SWITCH, W/ Back Box | FIKE | 10‐2963 | NOS | 6 | 435 | 125 | 0 | 750 | 0 | FALSE |  |  | 0 | NULL
1.2.1.6 |  | STI WEATHERPROOF COVER FOR SWITCHES (IP54) | STI STOPPER | STI 3150 | NOS | 6 | 352 | 101 | 0 | 606 | 0 | FALSE |  |  | 0 | NULL
1.2.1.7 |  | ABORT SWITCHES, c/w Back box | FIKE | 10-1639 | NOS | 2 | 360 | 103 | 0 | 206 | 0 | FALSE |  |  | 0 | NULL
1.2.1.8 |  | ABORT SWITCH (1 X MUSHROOM HEAD LATCHING -1 NO. + 1 NO. EMERGENCY STOP - FLAMEPROOF | E2S | STEXCP8PT-S-D-L-A-S-3-A1-R | NOS | 4 | 7250 | 2075 | 0 | 8300 | 0 | FALSE |  |  | 0 | NULL
1.2.1.9 |  | HORN STROBE, WALL MOUNTED - WEATHER PROOF | E2S | SH-HSOR | NOS | 8 | 215 | 62 | 0 | 496 | 0 | FALSE |  |  | 0 | NULL
1.2.1.10 |  | EXPLOSION PROOF STROBE HORN | E2S | BExCS11005-DPR-DC024-A-N-3-A1-R-R | NOS | 2 | 5250 | 1503 | 0 | 3006 | 0 | FALSE |  |  | 0 | NULL
1.2.1.11 |  | BELL, 6" WITH BACKBOX | SHIELD | FB-1000C6 | NOS | 2 | 85 | 25 | 0 | 50 | 0 | FALSE |  |  | 0 | NULL
1.2.1.12 |  | EXPLOSION PROOF BELL, 6" WITH BACKBOX | SECUTRON | CVX10-115VAC-R | NOS | 4 | 1500 | 430 | 0 | 1720 | 0 | FALSE |  |  | 0 | NULL
1.2.1.13 |  | ILLUMINATED WARNING SIGN "DONT ENTER GAS DISCHARGED" - WEATHER PROOF | SHIELD/AMPAC | SK27202/ Enclsoure: 4210-0120 & Fascia Plate: 4210-013 | NOS | 6 | 2750 | 787 | 0 | 4722 | 0 | FALSE |  |  | 0 | NULL
1.2.1.14 |  | ILLUMINATED WARNING SIGN "DONT ENTER GAS DISCHARGED" | SHIELD/AMPAC | SK27202/ Enclsoure: 4210-0120 & Fascia Plate: 4210-013 | NOS | 6 | 2750 | 787 | 0 | 4722 | 0 | FALSE |  |  | 0 | NULL
1.2.1.15 |  | REMOTE INDICATOR | SYSTEM SENSOR | RA100Z | NOS | 22 | 100 | 29 | 0 | 638 | 0 | FALSE |  |  | 0 | NULL
1.2.1.16 |  | RELEASE CONTROL MODULE W/ ISOLATOR BASE | FIKE | 55 -053 | NOS | 16 | 1140 | 327 | 0 | 5232 | 0 | FALSE |  |  | 0 | NULL
1.2.1.17 |  | MINI MONITOR MODULE W/ ISOLATOR BASE | FIKE | 55 -050 | NOS | 6 | 340 | 98 | 0 | 588 | 0 | FALSE |  |  | 0 | NULL
1.2.1.18 |  | MONITOR MODULE W/ ISOLATOR | FIKE | 55 -046 | NOS | 36 | 380 | 109 | 0 | 3924 | 0 | FALSE |  |  | 0 | NULL
1.2.1.19 |  | CONTROL MODULE W/ ISOLATOR | FIKE | 55 -047 | NOS | 34 | 435 | 125 | 0 | 4250 | 0 | FALSE |  |  | 0 | NULL
1.2.1.20 |  | POWER SUPPLY UNIT, 24V DC ,10 Amps, W / battery | FIKE | 10-2829-1-0-01-0-1-01 | NOS | 2 | 1676 | 480 | 0 | 960 | 0 | FALSE |  |  | 0 | NULL
1.2.1.21 |  | CRM4 RELAY MDOULE WITH ISOLATOR WITH BACKBOX | FIKE | 10-2204 | NOS | 2 | 548 | 157 | 0 | 314 | 0 | FALSE |  |  | 0 | NULL
1.2.1.22 |  | MAIN RESERVE SELECTOR SWITCH WITH BACKBOX | FIKE | 10-2967 | NOS | 1 | 345 | 99 | 0 | 99 | 0 | FALSE |  |  | 0 | NULL
1.2.1.23 |  | SOLENOID DISCONNECTOR SWITCH | FIKE | RCDS-1 | NOS | 1 | 500 | 144 | 0 | 144 | 0 | FALSE |  |  | 0 | NULL
1.3 |  | MECHANICAL COMPONENTS (MAIN) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
1.3.1 |  | 140 LITER, 300 BAR INERT GAS CYLINDER - MODEL: NF IG541-300-140 - NAFFCO COMPLETE WITH: - 140 LITER 356 MM DIA. CYLINDER FILLED WITH FILLED WITH IG-100 AGENT - 300 BAR DISCHARGE HEAD VALVE WITH PRESSURE GAUGE/PRESSURE SWITCH FOR 300 BAR; SAFETY PROTECTION CAP - CYLINDER ID LABEL FOR 300 BAR, IG 100 GAS, 140 LITER CONSTANTS PRESSURE REGULATOR FOR 200/300 BAR WITH GASKET | NAFFCO | NF IG100-300-140 | SETS | 31 | 4770 | 1365 | 0 | 42315 | 0 | FALSE |  |  | 0 | NULL
1.3.2 | 10341512133 | ELECTRO MAGNETIC DEVICE WITH DIODE, INLET THREADED TO M42 X 1.5, 24V DC, 0.5 A, IP 65 RATED, P/N.# B04425146 FOR UL LISTED FIRE SUPPRESSION SYSTEM (REFER ITEM.# 10341512136) | NAFFCO | B04425148 | NOS | 4 | 790 | 227 | 0 | 908 | 0 | FALSE |  |  | 0 | NULL
1.3.3 | 10341512120 | MANUAL / PNEUMATIC RELEASE DEVICE, WP 300 BAR, INLET THREADED TO M42 X 1.5, PNEUMATIC LINE CONNECTION G 1/8", P/N.# B04420065-NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B04420065 | NOS | 4 | 120 | 35 | 0 | 140 | 0 | FALSE |  |  | 0 | NULL
1.3.4 | 10341512122 | PNEUMATIC RELEASE DEVICE, WP 300 BAR, INLET THREADED TO M42 X 1.5, PNEUMATIC LINE CONNECTION G 1/8", P/N.# B04420066NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B04420066 | NOS | 27 | 80 | 23 | 0 | 621 | 0 | FALSE |  |  | 0 | NULL
1.3.5 | 10343512025 | DISCHARGE HOSE, DN16, WP 350 BAR, B/P 1400 BAR, 400MM LENGTH, INLET FEMALE THREAD TO W 21.8 X 1/14" TO DIN 477 & OUTLET FEMALE THREAD TO G 3/4", P/N.# B06920225-NF FOR NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM | NAFFCO | B06920225-NF | NOS | 31 | 180 | 52 | 0 | 1612 | 0 | FALSE |  |  | 0 | NULL
1.3.6 | 10343512032 | PILOT HOSE, SYNTHETIC RUBBER OIL RESISTANT W/STRAIGHT FITTINGS M12 X 1.5 FEMALE THREAD IN BOTH ENDS, 700MM LONG, W/P 400 BAR, B/P 1600 BAR, TEMP RANGE: -40 C. TO 100 C, P/N.# B06920212 FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B06920212-NF | NOS | 12 | 70 | 21 | 0 | 252 | 0 | FALSE |  |  | 0 | NULL
1.3.7 | 10343512033 | PILOT HOSE, SYNTHETIC RUBBER OIL RESISTANT W/STRAIGHT FITTINGS M12 X 1.5 FEMALE THREAD IN BOTH ENDS, 500MM LONG, W/P 400 BAR, B/P 1600 BAR, TEMP RANGE: -40 C. TO 100 C, P/N.# B06920213 FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | B06920213-NF | NOS | 18 | 70 | 21 | 0 | 378 | 0 | FALSE |  |  | 0 | NULL
1.3.8 | 10346012640 | BLEED VALVE, P/N.# 029730040-NF FOR UL LISTED FIRE SUPPRESSION SYSTEM | NAFFCO | 029730040 | NOS | 4 | 170 | 49 | 0 | 196 | 0 | FALSE |  |  | 0 | NULL
1.3.9 |  | MANIFOLD FOR 3 CYLINDER NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM, 360 DIA CYLINDER, P/N.# NFIG-360-SRM3 - NAFFCO | NAFFCO | NFIG-360-SRM3 | NOS | 2 | 880 | 252 | 0 | 504 | 0 | FALSE |  |  | 0 | NULL
1.3.10 | 10344012325 | MANIFOLD FOR 5 CYLINDER NAFFCOINERT UL CLEAN AGENT FIRE SUPPRESSION SYSTEM, 360 DIA CYLINDER, P/N.# NFIG-360-SRM5 - NAFFCO | NAFFCO | NFIG-360-SRM5 | NOS | 5 | 1060 | 304 | 0 | 1520 | 0 | FALSE |  |  | 0 | NULL
1.3.11 | 15466240212 | PRESSURE RELIEF DAMPER, SIZE: 1120 X 1120 X 120MM, MODEL: SHXUN1000 - AFP | AFP | SHXUN1000 | NOS | 4 | 5071.8648 | 1452 | 0 | 5808 | 0 | FALSE |  |  | 0 | NULL
2 |  | FOAM SYSTEM - GENERATOR & FUEL TANK ROOM |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
2.1 |  | MECHANICAL COMPONENTS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
2.1.1 | 10450515350 | FOAM BLADDER TANK, VERTICAL TYPE, CAPACITY: 100 GLN, RED COLOUR, UL LISTED - NAFFCO, UAE. | NAFFCO |  | SET | 1 | 19000 | 5436 | 0 | 5436 | 0 | FALSE |  |  | 0 | NULL
2.1.2 |  | AFFF FOAM CONCENTRATE - 3% | NAFFCO | NF3F-C6-AFFF | GALLONS | 77 | 30.28 | 9 | 0 | 693 | 0 | FALSE |  |  | 0 | NULL
2.1.3 |  | 3" DELUGE VALVE COMPLETE WITH: BASIC TRIM, ELECTRIC TRIM, 24V DC SOLENOID VALVE, MANUAL RELEASE, WATER MOTOR ALARM GONG, PRESSURE SWITCH, MAIN DRAIN VALVE, PRESSURE GAUGE | SHIELD | SD-DVA | SET | 1 | 4343 | 1243 | 0 | 1243 | 0 | FALSE |  |  | 0 | NULL
2.1.4 |  | OS&Y GATE VALVE 3" CLASS 125 FLANGED, 200 PSI WORKING UL/FM APPROVED | SHIELD | SD-OSY200FF-D | NOS | 1 | 510 | 146 | 0 | 146 | 0 | FALSE |  |  | 0 | NULL
2.1.5 | 10559022710 | TAMPER SWITCH (SUPERVISORY) WITH 1 X SPDT CONTACT FOR GATE VALVES, MODEL: SD-SVS OSY-1, UL/FM APPROVED - SHIELD | SHIELD | SD-SVS-OSY-1 | NOS | 1 | 167 | 48 | 0 | 48 | 0 | FALSE |  |  | 0 | NULL
2.1.6 |  | Y-STRAINER 3" CLASS 150 BOTH FLANGED ENDS, 300 PSI WORKING UL/ULC APPROVED WITH LISTED - FLANGED X FLANGED SS304 SCREEN -SHIELD | SHIELD | SD-YS300FF-D | NOS | 1 | 320 | 92 | 0 | 92 | 0 | FALSE |  |  | 0 | NULL
2.1.7 | 10556775100 | FOAM-WATER SPRINKLER 1/2 INCH BSPT BRONZE | NAFFCO | NH500 | NOS | 9 | 160 | 46 | 0 | 414 | 0 | FALSE |  |  | 0 | NULL
2.1.8 |  | 1" AIR RELEASE VALVE | NAFFCO |  | NOS | 1 | 221 | 64 | 0 | 64 | 0 | FALSE |  |  | 0 | NULL
2.2 |  | ELECTRICAL COMPONENTS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
2.2.1 |  | EXTINGUISHING CONTROL PANEL (2) DETECTION ZONE (1) RELEASE AREA COMPLETE WITH 24VDC BACK-UP BATTERY + CRM4 RELAY MODULE | SHIELD | AX-T | SET | 1 | 3500 | 954 | 0 | 954 | 0 | FALSE |  |  | 0 | NULL
2.2.2 |  | EXPLOSION PROOF UV/IR FLAME DETECTOR | REZONTECH | RFD-2000X | SET | 2 | 7500 | 2146 | 0 | 4292 | 0 | FALSE |  |  | 0 | NULL
2.2.3 |  | EXPLOSION PROOF BELL, 6" WITH BACKBOX | SECUTRON | CVX10-115VAC-R | NOS | 1 | 1500 | 430 | 0 | 430 | 0 | FALSE |  |  | 0 | NULL
2.2.4 |  | EXPLOSION PROOF STROBE HORN | E2S | BExCS11005-DPR-DC024-A-N-3-A1-R-R | NOS | 1 | 5250 | 1503 | 0 | 1503 | 0 | FALSE |  |  | 0 | NULL
2.2.5 |  | XENON/STROBE LIGHT WITH BACKBOX | SHIELD | SH-STOR | NOS | 1 | 180 | 52 | 0 | 52 | 0 | FALSE |  |  | 0 | NULL
2.2.6 |  | POWER SUPPLY UNIT, 24V DC ,10 Amps, W / battery | FIKE | 10-2829-1-0-01-0-1-01 | NOS | 2 | 1676 | 480 | 0 | 960 | 0 | FALSE |  |  | 0 | NULL
2.2.7 |  | WARNING SIGN | NAFFCO |  | SET | 1 | 300 | 86 | 0 | 86 | 0 | FALSE |  |  | 0 | NULL
3 |  | HIGH VELOCITY WATER SPRAY SYSTEM - TRANSFORMER ROOM - 4 NOS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
3.1 |  | 6" DELUGE VALVE COMPLETE WITH: BASIC TRIM, ELECTRIC TRIM, 24V DC SOLENOID VALVE, MANUAL RELEASE, WATER MOTOR ALARM GONG, PRESSURE SWITCH, MAIN DRAIN VALVE, PRESSURE GAUGE | SHIELD | SD-DVH2 | SET | 4 | 6673 | 1910 | 0 | 7640 | 0 | FALSE |  |  | 0 | NULL
3.2 |  | OS&Y GATE VALVE 6" CLASS 125 FLANGED, 250 PSI WORKING UL/FM APPROVED | SHIELD | SD-OSY250FF-D | NOS | 4 | 1000 | 287 | 0 | 1148 | 0 | FALSE |  |  | 0 | NULL
3.3 | 10559022710 | TAMPER SWITCH (SUPERVISORY) WITH 1 X SPDT CONTACT FOR GATE VALVES, MODEL: SD-SVS OSY-1, UL/FM APPROVED - SHIELD | SHIELD | SD-SVS-OSY-1 | NOS | 4 | 167 | 48 | 0 | 192 | 0 | FALSE |  |  | 0 | NULL
3.4 |  | HV SPRAY NOZZLE 3/4" BSPT/NPT SS FINISH, K-FACTOR:23, COVERAGE ANGLE: 120 DEG. UL LISTED - SHIELD | SHIELD | SDHV-AB | NOS | 256 | 93.1 | 27 | 0 | 6912 | 0 | FALSE |  |  | 0 | NULL
3.5 |  | PENDENT SPRINKLER HEAD 1/2" 79 DEG,STD RESP, BRASS FINISH, UL/ULC LISTED/FM APPROVED | SHIELD | SD1010SR | NOS | 208 | 9 | 3 | 0 | 624 | 0 | FALSE |  |  | 0 | NULL
3.6 |  | ACCESSORIES TO MANIFOLD - 2 NOS. OF 200MM DV |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | FALSE |  |  | 0 | NULL
3.7 |  | OS&Y GATE VALVE 8" CLASS 125 FLANGED, 250 PSI WORKING UL/FM APPROVED | SHIELD | SD-OSY250FF-D | NOS | 4 | 1590 | 455 | 0 | 1820 | 0 | FALSE |  |  | 0 | NULL
3.8 | 10559022710 | TAMPER SWITCH (SUPERVISORY) WITH 1 X SPDT CONTACT FOR GATE VALVES, MODEL: SD-SVS OSY-1, UL/FM APPROVED - SHIELD | SHIELD | SD-SVS-OSY-1 | NOS | 4 | 167 | 48 | 0 | 192 | 0 | FALSE |  |  | 0 | NULL
3.9 |  | Y-STRAINER 8" CLASS 150 BOTH FLANGED ENDS, 300 PSI WORKING UL/ULC APPROVED WITH LISTED - FLANGED X FLANGED SS304 SCREEN -SHIELD | SHIELD | SD-YS300FF-D | NOS | 4 | 1670 | 478 | 0 | 1912 | 0 | FALSE |  |  | 0 | NULL
3.10 |  | OS&Y GATE VALVE 2" BRONZE, 175 PSI, UL LISTED, MODEL: SDOSY-T 50, SHIELD | SHIELD | SDOSY-T | NOS | 4 | 510 | 146 | 0 | 584 | 0 | FALSE |  |  | 0 | NULL